Analysis and procedure for the energetic optimisation of pumps in water supply applications

„Pump check“

Rough check – method of calculation

Rough check – method of calculation

- Constants

Definition of

- acceleration of gravity

- density of water

- limit value for the acceptable difference of the phase currents

- lifetime of the pumps.

- Input: Sizing in general

  - Number of stages in case of high pressure pumps

    - Single stage low pressure pump

    - Multistage high pressure pump

      - Number of stages

  - Information about the water supply system

  - Kind of pump / design

  - Make / manufacturer

  - Serial number

  - Sizing data (read from nameplate)

    - Flow rate of the pump:		 	Q 		[l/s]

    - Pump head: 				H 		[m]

    - Mechanical rated motor power:	 	Pn= Pmech 	[W]
=> if Pmech > 375 kW => recommend a fine check.

    - Rated motor speed			nn 		[1/min]

    - Motor efficiency at nominal load		η mot  		[-]

    - Rated motor current 			In  		[A]

    - cos φn at nominal load	 		cos φn 		[-]

    - Rated motor voltage 			Un 		[V]

  - Kind of pump

    - Dry installed pump

    - Submersible pump

  - Operating hours per year in [h/a]

  - Energy costs in [CHF/a] (overall average)

- Measurement at running pump: duty point

  - Effective flow rate 				Qeff 		[l/s]

  - Measured pump head	 			ΔHdyn	  	[m]

  - Current measurement

    - Information about blind current compensation

    - Information about frequency converter incl. set frequency in [Hz]

    - Phase currents 				Iphase (3x)  	[A]

- General questions

  - Can it be seen from the motor / pump / complete system that renewal, optimization and/or reconstruction is needed?

  - Estimation of the repair/maintenance costs for the motor / pump / complete system)

  - Has the piping been changed? What have been changed?

- Calculation of total efficiency – actual value (processing of input values)

  - Calculation of the hydraulic power:

Phyd = Qeff* ΔHdyn *ρ*g 	[W] 	with: 	Q 	[m3/s]

ΔHdyn 	[m]

ρ 	[kg/m3]

g 	[m/s2]

  - Calculation of the electrical power:

Electrical power at nominal load:

Pelect,n = Un*In*√3*cos φn   [W]

Approximate calculation of power consumption with Tannerscher formula (see apendix „Rough check - Determination of the electrical power of an asynchronous motor“)

Approximate coefficient p0 = -0.3612 + 0.00251*Pn

Approximate coefficient px = 1.3644 - 0.002565* Pn

Load ratio Lv = Pelect / Pelect,n = p0 + px * mean value (I1,I2,I3) / In

Power consumption

Pelect = Lv * Pelect,n

  - Total efficiency:

η total,measured = Phydr / Pelect

- Calculation of total efficiency – optimal value

  - Number of pole pairs	ppz = round(3000/nn)

  - Spezific speed

nq = nn * √Qeff / H3/4 	with: 	n 				[1/min]

Qeff 				[m3/s]

H  = ΔHdyn/number of stages	[m]

    - Weighting according to impeller type: Table, which shows the maximal reachable hydraulic efficiency as a function of nq: ηhydr,max

    - Weighting according to frame size (Q): Smaller pumps have due to their construction a lower efficiency than larger pumps with the same speed (nq): fQ

    - Reduction in case of large number of stages with empiric coefficient fr

  - With the above mentioned influences the best possible pump efficiency can be calculated:

Ηpump, opt = ηhydr,max * fQ * fr

  - Optimal mechanical power:

Pmech, opt = Phyd / ηpump,opt

Best possible motor efficiency:

ηmot,opt in formula for Pmech,opt (reference table for dry installed pumps and circulator pumps)

  - Best possible total efficiency:

ηtot,opt = ηpump, opt * ηmotor,opt

- Results – Comparison of actual and optimal value

  - Energy efficiency (E coefficient)

E = η tot,measured / η tot,opt	(„How many % of the best possible total efficiency does the existing pump reaches at the duty point?“)

If E > 1 -> fault during data input

If E < 1 -> check is okay

Potential for optimization = 1 – E (expressed in %)

  - Potential for energy savings

Actual energy	Eact = Pelect * operating hours

Optimal energy	Eopt = Phyd / η tot,opt * operating hours

Potential for energy savings = Eact - Eopt in [kWh/a]

Potential for energy savings in % related to the actual condition = Potential for energy savings / Eact

  - Potential savings of energy costs (EK)

Actual energy costs per year	EKact = Pelect * operating hours * energy price

Optimal energy costs per year 	EKopt = Phyd / η tot,opt * operating hours * energy price

Annual savings of energy costs = EKact - EKopt

Savings of energy costs over the lifetime of the pump = Annual savings of energy costs * lifetime

  - Comparison sizing – measurements

Validation of pump head:
The result of the term (H - ΔHdyn) / H must not be more than 20 %.

Validation of flow rate:

The result of the term (Q - Qeff) / Q must not be more than 20 %.

Fine check: At least one of the following conditions must be fulfilled to recommend a fine check.

- Potential for optimization (6.1) > 10 %

- Pump head: Sizing data and measurement (6.4) shows a difference > 20 %

- Flow rate: Sizing data and measurement (6.4) shows a difference > 20 %

- Motor power (1.6.3) > 375 kW

- At least one of the general questions (3) have to be answered with YES, IN THE MEDIUM TERM or HIGH.

Caution: The whole test covers only the motor and pumps, but NOT all other system components and operating modes (system characteristic, management, ….)