Analysis and procedure for the energetic optimisation of pumps in water supply applications

„Pump check“

Fine check – instructions

Project pump check

“Fine check“

Pump and system analysis at a pump for determining the energetic and economic potential for optimization

Customer

Object

Pump

Pump type

Serial number

Order

Author

Fine check made by

Template and instructions for a fine check

This template and instructions specify the structure of the fine check, the minimum requirements to the data to be collected as well as their evaluation.

Disclaimer

This product has been developed for supporting the decision making process of energy-saving measures at pumps in water supply applications. A warranty for the correctness and completeness of the obtained results and information can not be given. Principally, any liabilities are excluded that are referred to material or more imaginary damages caused by the use or disuse of the presented information or the use of incorrect and incomplete data.

Contents

1	Summary	4

2	Starting situation, task	4

3	Data basis	4

4	Schematic overview of the results	4

5	Measurement setup / measured points / measurement parameters	4

5.1	Schematic illustration of the measurement object	4

5.2	Measuring instruments being used	4

5.3	Defined measurement procedure for the „fine check“	4

6	Measurement results in tabular form	5

6.1	Date, time and duration of the measurement process	5

6.2	Hydraulical measured data	5

6.3	Electrical measured data	5

6.4	Mechanical measurements at the motor and pump	5

6.5	General optical condition	5

7	Interpretation of the measurement results	5

7.1	Results of the rough check	5

7.2	Validation of the rough check results with data from own measurement	5

7.3	Analysis of the current duty point	5

7.4	Calculated curve for the „mechanical power requirements of the pump“	6

7.5	Comparison of the Q/H curve „fine check“ with the original curve	6

7.6	Evaluation of the electrical measured data	6

7.7	Evaluation of the mechanical condition of pump and motor	6

7.8	Evaluation of the general optical condition	6

7.9	Measurement accuracy or fault tolerance	6

8	Current operational concept	6

9	Possible measures for energy optimization	7

9.1	Energy-saving measures at pump/motor	7

9.2	Energy-saving measures by changing of operation	7

9.3	Cost-benefit calculation of the different variants of energy optimization measures	7

9.4	Recommendation for realization	7

10	Appendix	7

10.1	Hydraulic scheme and planning documents from the water supply company	7

10.2	Documentation of the existing pump	7

10.3	Documentation of the existing motor	7

10.4	List of the measurement instruments	7

10.5	Test report of the collected data	7

# Summary

What has been done?

Which water supply is affected?

Which pump is affected?

When has the fine check been made?

What is the result? (Be brief!)

# Starting situation, task

What is the aim and what can be expected from this fine check?

Reason for conducting the fine check.

What will be done within the fine check?

What will be not done within the fine check?

Where have problems arisen?

How was the procedure?

# Data basis

Which documents were available for the fine check?

Which documents were missing?

# Schematic overview of the results

Summary of the most important results of the measurements.

Summary of the recommended economic energy-saving measures together with the potential for savings in kWh/a and CHF/a.

# Measurement setup / measuring points / measurement parameters

  - Schematic illustration of the measurement object

Which pump is the measurement object?

Description of the inlet pressure with pressure losses -> inlet pressure at the pump

Description of the pump discharge -> discharge pressure at the pump

Geodetic pump heads

  - Measuring instruments being used

List of the measuring instruments being used, both fix (installed) and mobile. Indication of the respective measurement accuracy.

  - Defined measurement procedure for the „fine check“

At least:

- Measurement of the duty point (validation of rough check)

- Measurement of at least 3 duty points at differently closed insulating valve: Recording of the pump characteristic.

- Indication of the timing (new duty point, wait 5 minutes, measurement, …)

# Measurement results in tabular form

  - Date, time and duration of the measurement process

List the date, time and duration of the measurement process. The measurement has to correspond to the normal operating conditions.

  - Hydraulical measurement data

Hydraulical measurement data of the pump:

Aim is the determination of the hydraulic power Phydr

- Pressure measurement on the suction side

- Pressure measurement on the discharge side

- Stationary flowmetering (Inductive flowmeter)

- Mobile flowmetering (Ultrasonic flow measurement)

How and where are the respective measurement parameters collected?

  - Electrical measured data

Electrical measurement data of the motor:

Aim is the determination of the electrical power Pelec

- Phase voltages U

- Phase currents I

- Cos φ

- Insulating resistance of the windings

Caution: Blind current compensation and frequency converter! Soft starter?

How and where are the respective measurement parameters collected?

  - Mechanical measurements at the motor and pump

Mechanical measurement data:

- Frequency band recording of the body vibrations FFT

- Effective rated speed of the system

- Evaluation of cavitation at running pump

- Alignment of motor – pump

- Condition of anti-friction bearings

- Gaskets

How and where are the respective measurement parameters collected?

  - General optical condition

Description of the general optical condition: Running of pipes, high points, pipe cross sections, controls and instruments (age, maintenance), etc.

# Interpretation of the measurement results

  - Results of the rough check

Repetition of the results of the rough check: Voltage, current, pump head, flow rate, total efficiency and potential for optimization (both energetically and moneywise).

  - Validation of the rough check results with data from own measurement

Make a pump rough check with own collected data. Are there differences compared to the rough check the water supply company has made? If yes, what are the reasons? Which conclusions are to draw?

  - Analysis of the current duty point

Compare the current duty point with the sizing point on the basis of the measurement.

Interpretation of the differences, finding of the reasons.

  - Calculated curve for the „mechanical power requirements of the pump“

On the basis of the collected data only the total efficiency of the motor-pump unit can be determined. To determine the power requirements of the pump a calculation or estimation of the mechanical power requirements is needed. This is determined by means of the measured data, the motor condition, the control components (soft starter, frequency converter, compensation, etc.), the age of the motor, etc. That makes it possible to compare the calculated power requirements with the original power requirements of the pump, so that a statement about the pump quality can be made. The same applies for the comparison of the current efficiency of the pump with the original efficiency of the pump. However, it has to be point out, that it is an estimation only.

  - Comparison of the Q/H curve „fine check“ with the original curve

On the basis of the measured data the current pump curve is determined. Afterwards compare the current pump curve with the original pump curve. Interpretation of the differences, finding of the reasons.

  - Evaluation of the electrical measurement data

Evaluation of the points at 6.3:

  - Evaluation of the mechanical condition of pump and motor

Evaluation of the points at 6.4:

  - Evaluation of the general optical condition

Evaluation of the general optical condition (point 6.5): where is the potential for optimization?

  - Measurement accuracy or fault tolerance

Indication of the measurement accuracy of the various results.

# Current operational concept

Description of the current operational concept.

- When and how are the pumps running? Parallel operation? Redundances?

- Maintenance interval? Repair costs? Emergencies?

- How much water is pumped per year? What is the energy consumption?

- Does the operation vary according to the season?

# Possible measures for energy optimization

  - Energy-saving measures at pump/motor

Listing of the different economic energy-saving measures at the pump/motor.

  - Energy-saving measures by changing of operation

Listing of the different economic energy-saving measures by changing the operational concept.

  - Cost-benefit calculation of the different variants of energy optimization measures

Cost-benefit calculation of the mentioned energy-saving measures with evaluation and ranking.

The costs for the replacement pump and for the work to replace the pump have to be shown separately.

A combination of the different energy-saving measures is possible.

  - Recommendation for realization

Recommendation, which energy-saving measures should be implemented.

# Appendix

  - Hydraulic scheme and planning documents from the water supply company

  - Documentation of the existing pump

  - Documentation of the existing motor

  - List of the measuring instruments

  - Test report of the collected data